## Slide 1
SWaT Testbed

## Slide 2
Level 0 refers to the communication layer between sensors, actuators and the PLC. Level 0 includes a Remote IO (RIO) device. The RIO is connected to the physical sensors and actuators. Monitoring and control information is exchanged between the PLC, sensors, and actuators across a Distributed Logical Router (DLR).
Level 1 refers to the communication layer among PLCs. This layer is implemented in a star topology and includes a SCADA workstation, an HMI, and a Historian.

## Slide 3
Differential pressure sensors in Stage 3 measure the pressure drop across the UF unit. A backwash cycle is initiated when the pressure drop exceeds 0.4 bar indicating that the membranes need immediate cleaning. 1 bar = 100 kPa

## Slide 4
Each PLC obtains data from sensors associated with the corresponding stage, and controls pumps and valves in its domain.

## Slide 5
P301
P302
MV-301
FIT301
DPSH-301
PSH301
DPIH-301
LIT301
MV-302
MV-304
MV-303
Level Indication Transmitter (mm):UF feed water tank level
Low,Low Low,High,and High High

## Slide 6
P301
P302
MV-301
FIT301
DPSH-301
PSH301
DPIH-301
LIT301
MV-302
MV-304
MV-303
Actuator
UF Feed Pump
P301/ P302 | Pump water from UF feed water tank to RO feed water tank via UF filtration

## Slide 7
P301
P302
MV-301
FIT301
DPSH-301
PSH301
DPIH-301
LIT301
MV-302
MV-304
MV-303
Flow Indication Transmitter
(m3/hr):flow in UF stage

## Slide 8
P301
P302
MV-301
FIT301
DPSH-301
PSH301
DPIH-301
LIT301
MV-302
MV-304
MV-303
Differential Pressure Indicator Transmitter (kPa)
Control the back-wash process

## Slide 9
P301
P302
MV-301
FIT301
DPSH-301
PSH301
DPIH-301
LIT301
MV-302
MV-304
MV-303
Actuators
Motorised Valve
MV301 | Control UF-Backwash process
MV302 | Control water from UF process to De-Chlorination unit
MV303 | Control UF-Backwash drain
MV304 | Control UF drain